## Slide 1
Summary of Heat Loss Calculations
Assessing overall heating requirements for building (E)
Component | U-Value | Area | Heat Loss Rate (W oC-1)
Walls | Uwalls | Awalls | Uwalls * Awalls
Windows | Uwindows | Awindows | Uwindows * Awindows
Floor | Ufloor | Afloor | Ufloor * Afloor
Roof | Uroof | Aroof | Uroof * Aroof
 | Air change | Volume | 
Ventilation | ach | V | V * ach * 0.361
Total Heat Loss Rate H = ΣUx*Ax + V* ach * 0.361 |  |  | 
Annual Energy Requirement E = H * DegreeDays *86400
Degree Days are a measure of climate – for heating Degree Days are usually based on a base or neutral temperature of 15.5oC, 60oF. For cooling there is less agreement, but typically 22oC or 25oC.
The Fabric Heat Loss Parameter = = ΣUx*Ax
Heat Loss Rate and Heat Loss Parameter are used interchangeably
Heat Loss Coefficient is Heat Loss Parameter per unit area

## Slide 2
Summary of Energy Management in Buildings
Energy Management in Buildings - Heating
Chart: External Temperature oC
| -4 | -2 | 0 | 2 | 4 | 6 | 8 | 10 | 12 | 14 | 15.5 | 16 | 18 | 20 | 22
 | 193.8096 | 160.5736 | 159.819 | 132.967 | 116.0082 | 101.5835 | 71.6704 | 69.8886 | 41.0102 | 34.5762
 | 15.7688 | 13.4625 | 11.8598 | 15.832
 | 187.7727 | 170.0878 | 152.4029 | 134.718 | 117.0331 | 99.3482 | 81.6632 | 63.9783 | 46.2934 | 28.6085 | 15.3448
 | 159.6068 | 144.5747 | 129.5425 | 114.5103 | 99.4781 | 84.4459 | 69.4138 | 54.3816 | 39.3494 | 24.3172 | 13.0431
Do not include points > 15.5oC when defining trend line,
Red trend line may be used to predict future consumption,
Blue line takes account of efficiency of boiler,
Gradient of Blue Line is measured in kWh / day / oC
Divide by 24 (hrs) to get in kW and the gradient should be identical with Heat loss parameter
i.e. bottom up and top down approaches should give same answer.
Dashed Purple Line shows possible revised heat loss parameter after insulation improvement – e.g. double glazing
Dotted Black Line shows equivalent actual consumption after insulation measures
-can be compared with actual consumption
i.e. in this example actual savings are not what had been predicted

## Slide 3
Summary of Energy Management in Buildings
Temperature
Energy Consumption
Base Load
Heating

## Slide 4
Summary of Energy Management in Buildings
Temperature
Energy Consumption
Base Load
Heating
Cooling
Case with an electrically heated and cooled building – e.g. Shanghai

## Slide 5
Identify when consumption deviates significantly from trend line
1.5 standard deviations is a good starting point
Monitoring Performance – Gas

## Slide 6
Electricity Consumption in an Office Building in East Anglia
Consumption rose to nearly double level of early 2005.
Malfunction of Air-conditioning plant.
Extra fuel cost £12 000 per annum ~£1000 to repair fault
Additional CO2 emitted ~ 100 tonnes.
Low Energy Lighting Installed

## Slide 7
7
7
Good Management has reduced Energy Requirements
800
350
Space Heating Consumption reduced by 57%
CO2 emissions reduced by 17.5 tonnes per annum.
Performance of ZICER Building